## Sheet4
| OID |  |  | Description | Example
sysDescr | .1.3.6.1.2.1.1.1.0 | DisplayString | RO | Description | Switched PDU
sysObjectID | .1.3.6.1.2.1.1.2.0 | o (objid) | RO | Object | Enterprise.pdu
sysUptime | .1.3.6.1.2.1.1.3.0 | (timeticks) | RO | Time
sysContact | .1.3.6.1.2.1.1.4.0 | DisplayString | RO | Contact | Admin
sysName | .1.3.6.1.2.1.1.5.0 | DisplayString | RO | Name | PDU
sysLocation | .1.3.6.1.2.1.1.6.0 | DisplayString | RO | Location | Office
| .1.3.6.1.2.1.4.20 |  |  |  | IP Information, refer to APC
ipAdEntAddr | .1.3.6.1.2.1.4.20.1.1 | ipaddr
ipAdEntIfIndex | .1.3.6.1.2.1.4.20.1.2 | i (integer)
ipAdEntNetMask | .1.3.6.1.2.1.4.20.1.3 | ipaddr
ipAdEntBcastAddr | .1.3.6.1.2.1.4.20.1.4 | i (integer)
.1.3.6.1.2.1.4.20.1.5
PDU entry | .1.3.6.1.4.1.17420.1.2
pduID | .1.3.6.1.4.1.17420.1.2.1 | Integer | RO | The ID number of dev. |  | n/a
pduIP | .1.3.6.1.4.1.17420.1.2.2 | DisplayString | RW | static/192.168.2.122/255.255.255.0/192.168.2.254/192.168.2.254/ |  | IP/SUB/GATEWAY/DNS
pduMAC | .1.3.6.1.4.1.17420.1.2.3 | DisplayString | RO | 00:16:18:66:00:0e |  | MAC
pduVersion | .1.3.6.1.4.1.17420.1.2.4 | DisplayString | RO | 1.0-0425 |  | Firmware version
dev infor | .1.3.6.1.4.1.17420.1.2.5 | DisplayString | RO | Indicate the count of attached PDUs and their id. | 8,1,2,3,4,5,6,7,8 | PDU Total ID |  | Max. to 24
devValues | .1.3.6.1.4.1.17420.1.2.6 | DisplayString | RO | Indicate the PDU currents from PDU1 to PDU24 | 1,3,1,1,1,1,1,1 |  | Status '1=ON, 0= OFF, -2=Breaker Tripped, -1 = unavailable | Max. to 24
devTemperature1 | .1.3.6.1.4.1.17420.1.2.7 | Integer | RO | Temperateure1
devTemperature2 | .1.3.6.1.4.1.17420.1.2.7.1 | Integer | RO | Temperateure2
devHumidity1 | .1.3.6.1.4.1.17420.1.2.8 | Integer | RO | Humidity1
devHumidity2 | .1.3.6.1.4.1.17420.1.2.8.1 | Integer | RO | Humidity2
below is the rest of PDU circuit information
PDU table | .1.3.6.1.4.1.17420.1.2.9 |  |  | PDU
PDU01 entry | .1.3.6.1.4.1.17420.1.2.9.1 |  | RO |  |  | PDU ID=1
PDU01 value | .1.3.6.1.4.1.17420.1.2.9.1.11 | Integer | RO | Indicate the current of PDU-01 detect. | 1 | Total Current
PDU01 sub value | .1.3.6.1.4.1.17420.1.2.9.1.12 | DisplayString | RO | Indicate the outlet values (currents) from Bank1 to Bank8 | 0,-1,-1,-1,-1,-1,-1,-1 | Branch Current | -1 = unavailable | 無效
PDU01 outlet status | .1.3.6.1.4.1.17420.1.2.9.1.13 | DisplayString | RW | Indicate the outlet status/ Control Outlet | 1,0,0,0,0,0,0,0 | Outlet Control | Status '1=ON, 0= OFF, -2=Breaker Tripped, -1 = unavailable, 5= Ignore control command | Max. to 24
PDU01 outlet config table | .1.3.6.1.4.1.17420.1.2.9.1.14
| .1.3.6.1.4.1.17420.1.2.9.1.14.1 | DisplayString | RW | Indicate the configuration of Outlet1 | OutletA,0,0,0,0 | Outlet Name
pdu01Threshold1.0 | .1.3.6.1.4.1.17420.1.2.9.1.15 | Integer | RW | Indicate current warning threshold | 80
pdu01Threshold2.0 | .1.3.6.1.4.1.17420.1.2.9.1.16 | Integer | RW | Indicate current overload threshold | 100
Voltage.0 | .1.3.6.1.4.1.17420.1.2.9.1.17 | Integer | RW | Indicate voltage of PDU | 230
Model name.0 | .1.3.6.1.4.1.17420.1.2.9.1.18 | DisplayString | RO | Indicate PDU model name | POM | Model Name
pduModelNo.0 | .1.3.6.1.4.1.17420.1.2.9.1.19 | DisplayString | RO | PDU SD-1688 | PDU SD-1688 | Model Number
Identification.0 | .1.3.6.1.4.1.17420.1.2.9.1.20 | DisplayString | RW | Indicate PDU identify | PDU1
PDU01DelayOn | .1.3.6.1.4.1.17420.1.2.9.1.21 | String | RW | Indicate PDU Outlet On delay time. | 1 |  | Unit is second | Max. to 24
PDU01DelayOff | .1.3.6.1.4.1.17420.1.2.9.1.22 | String | RW | Indicate PDU Outlet Off delay time. | 1 |  | Unit is second | Max. to 24
PDU02 entry | .1.3.6.1.4.1.17420.1.2.9.2 |  | RO |  |  | PDU ID=2
PDU02 value | .1.3.6.1.4.1.17420.1.2.9.2.11 | Integer | RO | Indicate the current of PDU-01 detect. | 1 | Total Current
PDU02 outlet status | .1.3.6.1.4.1.17420.1.2.9.2.13 | DisplayString | RW | Indicate the outlet status/ Control Outlet | 1,0,0,0,0,0,0,0 | Outlet Control |  | Max. to 12
PDU02 outlet config table | .1.3.6.1.4.1.17420.1.2.9.2.14
| .1.3.6.1.4.1.17420.1.2.9.2.14.1 | DisplayString | RW | Indicate the configuration of Outlet1 | OutletB,0,0,0,0 | Outlet Name
pdu02Threshold1.0 | .1.3.6.1.4.1.17420.1.2.9.2.15 | Integer | RW | Indicate current warning threshold | 80
pdu02Threshold2.0 | .1.3.6.1.4.1.17420.1.2.9.2.16 | Integer | RW | Indicate current overload threshold | 100
PDU02DelayOn | .1.3.6.1.4.1.17420.1.2.9.2.21 | String | RW | Indicate PDU Outlet On delay time. | 2 |  |  | Max. to 12
PDU02DelayOff | .1.3.6.1.4.1.17420.1.2.9.2.22 | String | RW | Indicate PDU Outlet Off delay time. | 2 |  |  | Max. to 12
PDU03 entry | .1.3.6.1.4.1.17420.1.2.9.3 |  | RO
PDU03 value | .1.3.6.1.4.1.17420.1.2.9.3.11 | Integer | RO | Indicate the current of PDU-01 detect. | 1
PDU03 outlet status | .1.3.6.1.4.1.17420.1.2.9.3.12 | DisplayString | RW | Indicate the outlet status/ Control Outlet
PDU03 outlet config table | .1.3.6.1.4.1.17420.1.2.9.3.13
| .1.3.6.1.4.1.17420.1.2.9.3.14.1 | DisplayString | RW | Indicate the configuration of Outlet1 | OutletC,0,0,0,0
pdu03Threshold1.0 | .1.3.6.1.4.1.17420.1.2.9.3.15 | Integer | RW | Indicate current warning threshold | 80
pdu03Threshold2.0 | .1.3.6.1.4.1.17420.1.2.9.3.16 | Integer | RW | Indicate current overload threshold | 100
PDU03DelayOn | .1.3.6.1.4.1.17420.1.2.9.3.21 | String | RW | Indicate PDU Outlet On delay time. | 3
PDU03DelayOff | .1.3.6.1.4.1.17420.1.2.9.3.22 | String | RW | Indicate PDU Outlet Off delay time. | 3
PDU04 entry | .1.3.6.1.4.1.17420.1.2.9.4 |  | RO
PDU04 value | .1.3.6.1.4.1.17420.1.2.9.4.11 | Integer | RO | Indicate the current of PDU-01 detect. | 1
PDU04 outlet status | .1.3.6.1.4.1.17420.1.2.9.4.12 | DisplayString | RW | Indicate the outlet status/ Control Outlet
PDU04 outlet config table | .1.3.6.1.4.1.17420.1.2.9.4.13
| .1.3.6.1.4.1.17420.1.2.9.4.14.1 | DisplayString | RW | Indicate the configuration of Outlet1 | OutletD,0,0,0,0
pdu04Threshold1.0 | .1.3.6.1.4.1.17420.1.2.9.4.15 | Integer | RW | Indicate current warning threshold | 80
pdu04Threshold2.0 | .1.3.6.1.4.1.17420.1.2.9.4.16 | Integer | RW | Indicate current overload threshold | 100
DelayOn | .1.3.6.1.4.1.17420.1.2.9.4.21 | String | RW | Indicate PDU Outlet On delay time. | 4
DelayOff | .1.3.6.1.4.1.17420.1.2.9.4.22 | String | RW | Indicate PDU Outlet Off delay time. | 4
PDU08 entry | .1.3.6.1.4.1.17420.1.2.9.8 |  | RO
PDU08 value | .1.3.6.1.4.1.17420.1.2.9.8.11 | Integer | RO | Indicate the current of PDU-01 detect. | 1
PDU08 sub value | .1.3.6.1.4.1.17420.1.2.9.8.12 | DisplayString | RO
PDU08 outlet status | .1.3.6.1.4.1.17420.1.2.9.8.13 | DisplayString | RW | Indicate the outlet status/ Control Outlet
PDU08 outlet config table | .1.3.6.1.4.1.17420.1.2.9.8.14
| .1.3.6.1.4.1.17420.1.2.9.8.14.1 | DisplayString |  |  | OutletH,0,0,0,0
pduThreshold1.0 | .1.3.6.1.4.1.17420.1.2.9.8.15 | Integer | RW | Indicate current warning threshold | 80
pduThreshold2.0 | .1.3.6.1.4.1.17420.1.2.9.8.16 | Integer | RW | Indicate current overload threshold | 100
DelayOn | .1.3.6.1.4.1.17420.1.2.9.8.21 | String | RW | Indicate PDU Outlet On delay time. | 8
DelayOff | .1.3.6.1.4.1.17420.1.2.9.8.22 | String | RW | Indicate PDU Outlet Off delay time. | 8
Misc.
SNMPConfig | .1.3.6.1.4.1.17420.1.2.11
HeartBeatTrap | .1.3.6.1.4.1.17420.1.2.11.1 | DisplayString | RW | Enable Device Heartbeat to specific IP | XSSSS |  | X=0 disable, X=1 enable SSSS is heartbeat interval, unit is second | 09999 or 10001
EventTrapReceiver | .1.3.6.1.4.1.17420.1.2.11.2 | DisplayString
EventTrapReceiver1 | .1.3.6.1.4.1.17420.1.2.11.2.1 | DisplayString | RW | v1 Trap Receiver IP 1 | X,Y,Z |  | X = 0 disable , X=1 enable Y=ipaddress Z=community
EventTrapReceiver2 | .1.3.6.1.4.1.17420.1.2.11.2.2 | DisplayString | RW | v1 Trap Receiver IP 2 | X,Y,Z
EventTrapReceiver3 | .1.3.6.1.4.1.17420.1.2.11.2.3 | DisplayString | RW | v1 Trap Receiver IP 3 | X,Y,Z
EventTrapReceiver4 | .1.3.6.1.4.1.17420.1.2.11.2.4 | DisplayString | RW | v1 Trap Receiver IP 4 | X,Y,Z
EventTrapReceiver5 | .1.3.6.1.4.1.17420.1.2.11.2.5 | DisplayString | RW | v3 Trap Receiver IP 1 | A,B,C,D,E,F,G,H |  | A= 0 disable , A=1 enable B=user C=ipaddress D=securityLevel 0=noauth 1=auth 2=authPriv E=authProtocol 0=MD5 1=SHA F=password G=privProtocol 0=AES 1=DES H=PASSPHRASE
EventTrapReceiver6 | .1.3.6.1.4.1.17420.1.2.11.2.6 | DisplayString | RW | v3 Trap Receiver IP 2 | A,B,C,D,E,F,G,H
EventTrapReceiver7 | .1.3.6.1.4.1.17420.1.2.11.2.7 | DisplayString | RW | v3 Trap Receiver IP 3 | A,B,C,D,E,F,G,H
EventTrapReceiver8 | .1.3.6.1.4.1.17420.1.2.11.2.8 | DisplayString | RW | v3 Trap Receiver IP 4 | A,B,C,D,E,F,G,H
Circuit Current
PDUCircuitThreshold | .1.3.6.1.4.1.17420.1.2.12
DeviceWarning | .1.3.6.1.4.1.17420.1.2.12.1.10 | Integer | RW | Indicate total PDU warning threshold |  |  | unit A divide by 100
DeviceOverlaod | .1.3.6.1.4.1.17420.1.2.12.2.10 | Integer | RW | Indicate total PDU overload threshold |  |  | unit A divide by 100
DeviceBelow | .1.3.6.1.4.1.17420.1.2.12.3.10 | Integer | RW | Indicate total PDU overload threshold |  |  | unit A divide by 100
DeviceCurrent | .1.3.6.1.4.1.17420.1.2.13.10 | Integer | RO | Indicate total PDU current consumption |  |  | unit A divide by 100
DeviceCurrentInforamtion | .1.3.6.1.4.1.17420.1.2.14 | String | RO | Indicate the PDU Configuration | phase,circuit,outlet
ENV Threshold
TemperatureUnit | .1.3.6.1.4.1.17420.1.4.30.0 | String | RO | Indicate temperature unit, C or F | C |  | C is Celsius, F is Fahrenheit
temp1Lower | .1.3.6.1.4.1.17420.1.4.42.0 | Integer | RW | Indicate temperature lower threshold ENV1 | 1 |  | unit is celsius degree
temp1Upper | .1.3.6.1.4.1.17420.1.4.43.0 | Integer | RW | Indicate temperature upper threshold ENV1 | 100 |  | unit is celsius degree
humidity1Lower | .1.3.6.1.4.1.17420.1.4.44.0 | Integer | RW | Indicate humidity lower threshold ENV1 | 1 |  | unit is %
humidity1Upper | .1.3.6.1.4.1.17420.1.4.45.0 | Integer | RW | Indicate humidity upper threshold ENV1 | 100 |  | unit is %
temp2Lower | .1.3.6.1.4.1.17420.1.4.46.0 | Integer | RW | Indicate temperature lower threshold ENV2 | 1 |  | unit is celsius degree
temp2Upper | .1.3.6.1.4.1.17420.1.4.47.0 | Integer | RW | Indicate temperature upper threshold ENV2 | 100 |  | unit is celsius degree
humidity2Lower | .1.3.6.1.4.1.17420.1.4.48.0 | Integer | RW | Indicate humidity lower threshold ENV2 | 1 |  | unit is %
humidity2Upper | .1.3.6.1.4.1.17420.1.4.49.0 | Integer | RW | Indicate humidity upper threshold ENV2 | 100 |  | unit is %
below is Trap
| .1.3.6.1.4.1.17420.0.110 | Information |  | Device Back to Normal | Device Name, " " event cleared
| .1.3.6.1.4.1.17420.0.111 | Critical |  | PDU Current Overload Occur | Devicel Name, Toatl/Phase#/Circuit#/Outlet# Amp
| .1.3.6.1.4.1.17420.0.112 | Warning |  | PDU Current Warning Occur | Devicel Name, Toatl/Phase#/Circuit#/Outlet# Amp
| .1.3.6.1.4.1.17420.0.113 | Information |  | Configuration Change | Devicel Name, Configuration has been changed
| .1.3.6.1.4.1.17420.0.114 | Information |  | PDU Outlet On in ## secound | Devicel Name, Outlet# is switched on
| .1.3.6.1.4.1.17420.0.115 | Information |  | PDU Outlet Off | Devicel Name, Outlet# is switched off
| .1.3.6.1.4.1.17420.0.116 | Critical |  | PDU Output fault | Devicel Name, Outlet# fault
| .1.3.6.1.4.1.17420.0.117 | Information |  | Web user Loggin | Web user [snmp] logged in from IP
| .1.3.6.1.4.1.17420.0.118 | Critical |  | ATS Input fails | Devicel Name, Input# fails
| .1.3.6.1.4.1.17420.0.119 | Information |  | ATS Input source switched | Devicel Name, Input is changed to Input #
| .1.3.6.1.4.1.17420.0.120 | Critical |  | ATS input restored | Devicel Name, Input# is restored
| .1.3.6.1.4.1.17420.0.121 | Information |  | Heartbeat: Deivce is alive | Device Name is alive
| .1.3.6.1.4.1.17420.0.122 | Information |  | Temperature out of lower threshold | Device Name, Temperature out of lower threshold, #C
| .1.3.6.1.4.1.17420.0.123 | Information |  | Humidity out of lower threshold | Device Name, Humidity out of lower threshold, #%
| .1.3.6.1.4.1.17420.0.124 | Information |  | Temperature out of higher threshold | Device Name, Temperature out of higher threshold, #C
| .1.3.6.1.4.1.17420.0.125 | Information |  | Humidity out of higher threshold | Device Name, Humidity out of higher threshold, #%
| .1.3.6.1.4.1.17420.0.126 | Information |  | DO # Open | DO # Open
| .1.3.6.1.4.1.17420.0.127 | Information |  | DO # Close | DO # Close
| .1.3.6.1.4.1.17420.0.128 | Information
| .1.3.6.1.4.1.17420.0.129 | Information
| .1.3.6.1.4.1.17420.0.130 | Information |  | DI # Open | DI # Open
| .1.3.6.1.4.1.17420.0.131 | Information |  | DI # Close | DI # Close
| .1.3.6.1.4.1.17420.0.132 | Information |  | PDU Start Counting for Ping Action | Device Name, Start Counting for Ping Action
| .1.3.6.1.4.1.17420.0.133 | Information |  | Door Access Authentication Failure | Device Name, Door Access Authentication Failure
| .1.3.6.1.4.1.17420.0.134 | Critical |  | Breaker is Tripped | Device Name, Breaker# is Tripped
| .1.3.6.1.4.1.17420.0.135 | Critical |  | PDU Current Overload Removed | Devicel Name, Toatl/Phase#/Circuit#/Outlet# Amp
| .1.3.6.1.4.1.17420.0.136 | Information |  | PDU Outlet On after ## seconds | Devicel Name, Outlet# is powered on after ## seconds
| .1.3.6.1.4.1.17420.0.137 | Information |  | PDU Outlet Off after ## seconds | Devicel Name, Outlet# is powered off after ## seconds